## FUS 2020 (Table 5)
City of Barrie Fire Flow Calculator Per Fire Underwriters Survey (2020)
Please see Fire Underwriter Survey in the link below for additional details.
Water Supply for Public Fire Protection in Canada (Fire Underwriters Survey)
Disclaimer: The City does not guarantee that this form will suit each individual scenario/analysis. Where incompatibilities are encountered the requirements of the FUS and regulating documents shall prevail over the input and outputs of the FUS Calculator.
Project Address: | XYZ Development Project - 70 Collier St |  |  |  | Prepared by: | Fernando E.
Proposed Building | [Enter Building Name/ID] |  |  |  | Checked by: | Olu A.
Project No.: | 2026-XXXX |  |  |  | Date: | 2026-02-27
An estimate of fire flow required for a given area may be determined by the formula:
Where:
RFF = the required fire flow in litres per minute (L/min)
C = the construction coeficcient is related to the type of construction of the building
|  |  | Type I – Fire Resistive |  | 0.6
|  |  | Type II – Non-combustible |  | 0.8
|  |  | Type III – Ordinary |  | 1
|  |  | Type IV-A – Encapsulated MT |  | 0.8
|  |  | Type IV-B – Rated MT |  | 0.9
|  |  | Type IV-C – Ordinary MT |  | 1
|  |  | Type IV-D – Unrated MT |  | 1.5
|  |  | Type V – Wood Frame |  | 1.5
A = the total effective floor area (effective building area) in square metres (excluding basements at least 50 percent below grade) in the building considered)
STEP A: |  | Construction Coefficient (C)* | Select here |  | 0
STEP B: | Total Effective Floor Area
Choose Yes/No
|  |  | Is basement at least 50 % below grade?* |  | Select here |  | If yes, basement floor area excluded
|  |  | Vertical opening protected?* |  | Select here |  | *For consideration for effective area calculations
Calculate Effective Floor Area based on the highlighted statement
-C value from 1.0 to 1.5: 100% of all floor areas are used
-C value below 1 and vertical openings are not protected: Consider two largest floors plus 50 % of all floor above to a max of eight
-C value below 1 and vertical opening are protected: Consider single largest floor plus 25% of the two immediately adjoining floors
*A building may be subdivided if there is a vertical firewall with a fire-resistance rating greater than 2 hours (as per the OBC). This would meet the requirements of the NBC for separate building.
|  | Floors Above Grade | Total Floor Area (m²)* |  | % of Area Considered* |  | Effective Floor Area (m²)
|  | Basement | 0 |  | 0% |  | 0
|  | Ground Floor | 0 |  | 0% |  | 0
|  | Level 2 | 0 |  | 0% |  | 0
|  | Level 3 | 0 |  | 0% |  | 0
|  | Level 4 | 0 |  | 0% |  | 0
|  | Level 5 | 0 |  | 0% |  | 0
|  | Level 6 | 0 |  | 0% |  | 0
|  | Level 7 | 0 |  | 0% |  | 0
|  | Level 8 | 0 |  | 0% |  | 0
|  | Level 9 | 0 |  | 0% |  | 0
|  | Level 10 | 0 |  | 0% |  | 0
|  | Total |  |  |  |  | 0
STEP C: |  |  | Total Effective Floor Area |  | 0 |  | m²
|  |  | Therefore RFF = |  | 0 |  | L/min (rounded to the nearest 1000 L/min)
STEP D: | Occupancy Contents Adjustment Factor
The required fire flow may be reduced by as much as -25% for occupancies having contents with very low fire hazard or may be increased by up to 25% surcharge for occupancies having a high fire hazard
Occupancy and Contents Adjustments Factor
|  |  | Non-Combustible |  | -25%
|  |  | Limited Combustible |  | -15%
|  |  | Combustible |  | 0%
|  |  | Free Burning |  | 15%
|  |  | Rapid Burning |  | 25%
-Refer to Table 3 for recommended Occupancy and Contents Charges by major occupancy examples
|  |  | Type of Occupancy* |  | Adjustment Factor
|  |  | Select here |  | 0%
|  |  | Total Reduction % |  | 0 |  | L/min (reduction)
|  |  | RFF = |  | 0 |  | L/min (not rounded)
Note: The RFF flow calculated at this stage is used in Step E and F
STEP E: | Automatic Sprinkler Protection
Sprinklers - The required fire flow may be reduced by up to 50% for complete automatic sprinkler protection depending upon adequancy of system.
[5 empty] | Choose Yes/No |  | Possible Reduction Available | Actual Reduction Provided
| Automatic sprinkler protection designed and installed in accordance with NFPA 13?* |  |  |  | Select here |  | -30% | 0%
| Water supply is standard for both the system and Fire Department Connection (Siamese)?* |  |  |  | No |  | -10% | 0%
| Fully supervised system?* |  |  |  | No |  | -10% | 0%
-Reduction available assumes complete building coverage
-30% reduction typical for building requiring sprinkler system
|  |  | Total Reduction % |  | 0% |  | (reduction)
|  |  | Total Reduced Flow |  | 0 |  | L/min (reduction, not rounded)
STEP F: | Exposure Adjustment Charge: If full building details are not available, use FUS (Table 5) for the exposure adjustment
Exposure - A percentage of water for the exposures should be added to the required fire flow for the subject building to provide adequate flow rates for hose streams used to reduce the spreading of fire from the subject building to exposed risks. The required fire flow of a subject building may be increased depending on the severity of exposed risks to the subject building and the distance between the exposed risks and the subject building. This charge considers the usage of water supplies to prevent exposed risks from igniting or being damaged during a major fire incident in the subject building.
|  |  | Separation Distance |  | Maximum Exposure Adjustment Charge
|  |  | 0 to 3m |  | 25%
|  |  | 3.1 to 10m |  | 20%
|  |  | 10.1 to 20m |  | 15%
|  |  | 20.1 to 30m |  | 10%
|  |  | Greater than 30m |  | 0%
*If a vertical fire wall is properly constructed and has a rating of no less than 2 hours, then the boundary can be treated as protected with no exposure charge.
*The maximum exposure adjustment charge to be applied to a subject building is 75%.
*The distance in metres from the subject building facing wall to the exposed building facing wall, measured to the nearest metre, between the nearest points of the buildings. Where either the subject building or the exposed building is at a diagonal to the other building, the shortest distance should be increased by 3 metres and this adjusted value used as exposure distance.
*Refer to Table 5 for Exposure Charges
| Exposed Buildings |  | Description* |  | Distance (m)* |  | Surcharge Factor | Surcharge (L/min)
| North |  |  |  | 12 |  | 15% | 0
| East |  |  |  | 23 |  | 10% | 0
| South |  |  |  | 10 |  | 20% | 0
| West |  |  |  | 7 |  | 20% | 0
|  |  | Total Surcharged Flow |  | 0 |  | L/min (not rounded)
STEP G: | Final Required Fire Flow
|  | Step D- Occupancy Adjusted Fire Flow Demand |  |  | 0 | L/min
|  |  | Step E - Sprinkler Reduction |  | 0 | L/min
|  |  | Step F - Exposure Surcharge |  | 0 | L/min
|  |  | Final Fire Flow |  | 0 | L/min
[5 empty] | 0 | L/min (rounded to the nearest 1000L/min)
|  |  | or |  | 0 | L/s
|  |  | or |  | 0 | USGPM
|  |  | Required duration |  | 1 | hours
*Refer to table 1 for Duration
𝑅𝐹𝐹=220𝐶√𝐴

## FUS 2020 (Table 6)
City of Barrie Fire Flow Calculator Per Fire Underwriters Survey (2020)
Please see Fire Underwriter Survey in the link below for additional details.
Water Supply for Public Fire Protection in Canada (Fire Underwriters Survey)
Disclaimer: The City does not guarantee that this form will suit each individual scenario/analysis. Where incompatibilities are encountered the requirements of the FUS and regulating documents shall prevail over the input and outputs of the FUS Calculator.
Project Address: | XYZ Development Project - 70 Collier St | [5 empty] | Prepared by: | Fernando E.
Proposed Building | [Enter Building Name/ID] | [5 empty] | Checked by: | Olu A.
Project No.: | 2026-XXXX | [5 empty] | Date: | 2026-02-27
An estimate of fire flow required for a given area may be determined by the formula:
Where:
RFF = the required fire flow in litres per minute (L/min)
C = the construction coeficcient is related to the type of construction of the building
[5 empty] | Type I – Fire Resistive |  | 0.6
[5 empty] | Type II – Non-combustible |  | 0.8
[5 empty] | Type III – Ordinary |  | 1
[5 empty] | Type IV-A – Encapsulated MT |  | 0.8
[5 empty] | Type IV-B – Rated MT |  | 0.9
[5 empty] | Type IV-C - Ordinary MT |  | 1
[5 empty] | Type IV-D – Unrated MT |  | 1.5
[5 empty] | Type V – Wood Frame |  | 1.5
A = the total effective floor area (effective building area) in square metres (excluding basements at least 50 percent below grade) in the building considered)
STEP A: | Construction Coefficient (C)* |  |  |  | Select here |  | 0
STEP B: | Total Effective Floor Area
Choose Yes/No
[5 empty] | Is basement at least 50 % below grade?* |  | Select here |  | If yes, basement floor area excluded
[5 empty] | Vertical opening protected?* |  | Select here |  | *For consideration for effective area calculations
Calculate Effective Floor Area based on the highlighted statement
-C value from 1.0 to 1.5: 100% of all floor areas are used
-C value below 1 and vertical openings are not protected: Consider two largest floors plus 50 % of all floor above to a max of eight
-C value below 1 and vertical opening are protected: Consider single largest floor plus 25% of the two immediately adjoining floors
*A building may be subdivided if there is a vertical firewall with a fire-resistance rating greater than 2 hours (as per the OBC). This would meet the requirements of the NBC for separate building.
*In the case of high one-storey buildings (common in industrial zones), the building is considered a single storey for effective floor area calculations.
|  |  | Floors Above Grade |  | Total Floor Area (m²)* |  | % of Area Considered* |  | Effective Floor Area (m²)
|  |  | Basement |  | 0 |  | 0% |  | 0
|  |  | Ground Floor |  | 0 |  | 0% |  | 0
|  |  | Level 2 |  | 0 |  | 0% |  | 0
|  |  | Level 3 |  | 0 |  | 0% |  | 0
|  |  | Level 4 |  | 0 |  | 0% |  | 0
|  |  | Level 5 |  | 0 |  | 0% |  | 0
|  |  | Level 6 |  | 0 |  | 0% |  | 0
|  |  | Level 7 |  | 0 |  | 0% |  | 0
|  |  | Level 8 |  | 0 |  | 0% |  | 0
|  |  | Level 9 |  | 0 |  | 0% |  | 0
|  |  | Level 10 |  | 0 |  | 0% |  | 0
|  |  | Total | [5 empty] | 0
STEP C: |  |  |  |  | Total Effective Floor Area |  | 0 |  | m²
[5 empty] | Therefore RFF = |  | 0 |  | L/min (rounded to the nearest 1000 L/min)
STEP D: | Occupancy Contents Adjustment Factor
The required fire flow may be reduced by as much as -25% for occupancies having contents with very low fire hazard or may be increased by up to 25% surcharge for occupancies having a high fire hazard
Occupancy and Contents Adjustments Factor
[5 empty] | Non-Combustible |  | -25%
[5 empty] | Limited Combustible |  | -15%
[5 empty] | Combustible |  | 0%
[5 empty] | Free Burning |  | 15%
[5 empty] | Rapid Burning |  | 25%
-Refer to Table 3 for recommended Occupancy and Contents Charges by major occupancy examples
[5 empty] | Type of Occupancy* |  | Adjustment Factor
[5 empty] | Select here |  | 0%
[5 empty] | Total Reduction % |  | 0 |  | L/min (reduction)
[5 empty] | RFF = |  | 0 |  | L/min (not rounded)
Note: The RFF flow calculated at this stage is used in Step E and F
STEP E: | Automatic Sprinkler Protection
Sprinklers - The required fire flow may be reduced by up to 50% for complete automatic sprinkler protection depending upon adequancy of system.
[7 empty] | Choose Yes/No |  | Possible Reduction Available | Actual Reduction Provided
|  | Automatic sprinkler protection designed and installed in accordance with NFPA 13?* |  |  |  |  | Select here |  | -30% | 0%
|  | Water supply is standard for both the system and Fire Department Connection (Siamese)?* |  |  |  |  | Select here |  | -10% | 0%
[5 empty] | Fully supervised system?* |  | Select here |  | -10% | 0%
-Reduction available assumes complete building coverage
-30% reduction typical for building requiring sprinkler system
[5 empty] | Total Reduction % |  | 0% |  | (reduction)
[5 empty] | Total Reduced Flow |  | 0 |  | L/min (reduction, not rounded)
STEP F: | Exposure Adjustment Charge: If complete building information is available to determine the exposure adjustment, refer to FUS 2020 (Table 6).
Exposure - A percentage of water for the exposures should be added to the required fire flow for the subject building to provide adequate flow rates for hose streams used to reduce the spreading of fire from the subject building to exposed risks. The required fire flow of a subject building may be increased depending on the severity of exposed risks to the subject building and the distance between the exposed risks and the subject building. This charge considers the usage of water supplies to prevent exposed risks from igniting or being damaged during a major fire incident in the subject building.
*A length-height value of the exposed building facing wall should be determined by multiplying the length of the exposed building facing wall in metres by the height of the exposed building in stories. (Each 4 metres or fraction thereof equals one story for this determination.)
|  |  | Exposed Buildings |  | Length of the exposed building facing wall (m)* |  | Height of the exposed building in stories* |  | Length-Height Factor
|  |  | North | [5 empty] | 0
|  |  | South | [5 empty] | 0
|  |  | East | [5 empty] | 0
|  |  | West | [5 empty] | 0
*If a vertical fire wall is properly constructed and has a rating of no less than 2 hours, then the boundary can be treated as protected with no exposure charge.
*The maximum exposure adjustment charge to be applied to a subject building is 75%.
*The distance in metres from the subject building facing wall to the exposed building facing wall, measured to the nearest metre, between the nearest points of the buildings. Where either the subject building or the exposed building is at a diagonal to the other building, the shortest distance should be increased by 3 metres and this adjusted value used as exposure distance.
*Refer to table 6 for exposure adjustment charges for subject building considering construction type of exposed building face
| Exposed Buildings | Distance (m) to the exposure* |  |  | Length-Height Factor of exposing building face* |  | Type* |  | Surcharge Factor | Surcharge (L/min)
| North | Select here |  |  | Select here 2 |  | Select Here 3 |  | 0% | 0
| South | Select here |  |  | Select here 2 |  | Select Here 3 |  | 0% | 0
| East | Select here |  |  | Select here 2 |  | Select Here 3 |  | 0% | 0
| West | Select here |  |  | Select here 2 |  | Select Here 3 |  | 0% | 0
[5 empty] | Total Surcharged Flow |  | 0 |  | L/min (not rounded)
STEP G: | Final Required Fire Flow
[5 empty] | Step D- Occupancy Adjusted Fire Flow Demand |  | 0 | L/min
[5 empty] | Step E - Sprinkler Reduction |  | 0 | L/min
[5 empty] | Step F - Exposure Surcharge |  | 0 | L/min
[5 empty] | Final Fire Flow |  | 0 | L/min
[7 empty] | 0 | L/min (rounded to the nearest 1000L/min)
[5 empty] | or |  | 0 | L/s
[5 empty] | or |  | 0 | USGPM
[5 empty] | Required duration |  | 1 | hours
*Refer to table 1 for Duration
=
𝑯𝒆𝒊𝒈𝒉𝒕 𝒐𝒇 𝒕𝒉𝒆 𝒆𝒙𝒑𝒐𝒔𝒆𝒅 𝒃𝒖𝒊𝒍𝒅𝒊𝒏𝒈 𝒊𝒏 𝒔𝒕𝒐𝒓𝒊𝒆𝒔=
(𝟏𝟐 (𝒎))/(𝟒 (𝒎) ) =𝟑
*If the number of stories is known, enter it directly in the “Height of the Exposed Building in Stories” column.
*If the number of stories is unknown, refer to the calculation example below to determine the height in stories:
If the Height of exposed building is 12m.
𝑅𝐹𝐹=220𝐶√𝐴

## Tables (hidden)
Construction Type | Coefficient (C) | Total effective Area | Select here | Select here 2 | Select Here 3 | 0%
Select here | 0 | Select here | 0 to 3 | 0-20 | Type V | 20%
Type I – Fire Resistive | 0.6 | Yes | 0 to 3 | 0-20 | Type III-IV2 | 15%
Type II – Non-combustible | 0.8 | No | 0 to 3 | 0-20 | Type III-IV3 | 5%
Type III – Ordinary | 1 |  | 0 to 3 | 0-20 | Type I-II2 | 10%
Type IV-A – Encapsulated MT | 0.8 |  | 0 to 3 | 0-20 | Type I-II3 | 0%
Type IV-B – Rated MT | 0.9 |  | 0 to 3 | 21-40 | Type V | 21%
Type IV-C - Ordinary MT | 1 |  | 0 to 3 | 21-40 | Type III-IV2 | 16%
Type IV-D – Unrated MT | 1.5 |  | 0 to 3 | 21-40 | Type III-IV3 | 6%
Type V – Wood Frame | 1.5 |  | 0 to 3 | 21-40 | Type I-II2 | 11%
|  |  | 0 to 3 | 21-40 | Type I-II3 | 1%
|  |  | 0 to 3 | 41-60 | Type V | 22%
|  |  | 0 to 3 | 41-60 | Type III-IV2 | 17%
Type of Occupancy | Adjustment Factor |  | 0 to 3 | 41-60 | Type III-IV3 | 7%
Select here | 0% |  | 0 to 3 | 41-60 | Type I-II2 | 12%
Non-Combustible | -25% |  | 0 to 3 | 41-60 | Type I-II3 | 2%
Limited Combustible | -15% |  | 0 to 3 | 61-80 | Type V | 23%
Combustible | 0% |  | 0 to 3 | 61-80 | Type III-IV2 | 18%
Free Burning | 15% |  | 0 to 3 | 61-80 | Type III-IV3 | 8%
Rapid Burning | 25% |  | 0 to 3 | 61-80 | Type I-II2 | 13%
|  |  | 0 to 3 | 61-80 | Type I-II3 | 3%
Sprinkler |  |  | 0 to 3 | 81-100 | Type V | 24%
Select here | 0% |  | 0 to 3 | 81-100 | Type III-IV2 | 19%
Yes | -30% |  | 0 to 3 | 81-100 | Type III-IV3 | 9%
No | 0% |  | 0 to 3 | 81-100 | Type I-II2 | 14%
Unknown | 0% |  | 0 to 3 | 81-100 | Type I-II3 | 4%
|  |  | 0 to 3 | Over 100 | Type V | 25%
Select here | 0% |  | 0 to 3 | Over 100 | Type III-IV2 | 20%
Yes | -10% |  | 0 to 3 | Over 100 | Type III-IV3 | 10%
No | 0% |  | 0 to 3 | Over 100 | Type I-II2 | 15%
Unknown | 0% |  | 0 to 3 | Over 100 | Type I-II3 | 5%
Flow Required | Duration |  | 3.1 to 10 | 0-20 | Type V | 15%
0 | 1 |  | 3.1 to 10 | 0-20 | Type III-IV2 | 10%
3000 | 1.25 |  | 3.1 to 10 | 0-20 | Type III-IV3 | 3%
4000 | 1.5 |  | 3.1 to 10 | 0-20 | Type I-II2 | 6%
5000 | 1.75 |  | 3.1 to 10 | 0-20 | Type I-II3 | 0%
6000 | 2 |  | 3.1 to 10 | 21-40 | Type V | 16%
8000 | 2 |  | 3.1 to 10 | 21-40 | Type III-IV2 | 11%
10000 | 2 |  | 3.1 to 10 | 21-40 | Type III-IV3 | 4%
12000 | 2.5 |  | 3.1 to 10 | 21-40 | Type I-II2 | 7%
14000 | 3 |  | 3.1 to 10 | 21-40 | Type I-II3 | 0%
16000 | 3.5 |  | 3.1 to 10 | 41-60 | Type V | 17%
18000 | 4 |  | 3.1 to 10 | 41-60 | Type III-IV2 | 12%
20000 | 4.5 |  | 3.1 to 10 | 41-60 | Type III-IV3 | 5%
22000 | 5 |  | 3.1 to 10 | 41-60 | Type I-II2 | 8%
24000 | 5.5 |  | 3.1 to 10 | 41-60 | Type I-II3 | 1%
26000 | 6 |  | 3.1 to 10 | 61-80 | Type V | 18%
28000 | 6.5 |  | 3.1 to 10 | 61-80 | Type III-IV2 | 13%
30000 | 7 |  | 3.1 to 10 | 61-80 | Type III-IV3 | 6%
32000 | 7.5 |  | 3.1 to 10 | 61-80 | Type I-II2 | 9%
34000 | 8 |  | 3.1 to 10 | 61-80 | Type I-II3 | 2%
36000 | 8.5 |  | 3.1 to 10 | 81-100 | Type V | 19%
38000 | 9 |  | 3.1 to 10 | 81-100 | Type III-IV2 | 14%
40000 | 9.5 |  | 3.1 to 10 | 81-100 | Type III-IV3 | 7%
|  |  | 3.1 to 10 | 81-100 | Type I-II2 | 10%
|  |  | 3.1 to 10 | 81-100 | Type I-II3 | 3%
|  |  | 3.1 to 10 | Over 100 | Type V | 20%
|  |  | 3.1 to 10 | Over 100 | Type III-IV2 | 15%
|  |  | 3.1 to 10 | Over 100 | Type III-IV3 | 8%
|  |  | 3.1 to 10 | Over 100 | Type I-II2 | 11%
|  |  | 3.1 to 10 | Over 100 | Type I-II3 | 4%
|  |  | 10.1 to 20 | 0-20 | Type V | 10%
|  |  | 10.1 to 20 | 0-20 | Type III-IV2 | 5%
|  |  | 10.1 to 20 | 0-20 | Type III-IV3 | 0%
|  |  | 10.1 to 20 | 0-20 | Type I-II2 | 3%
|  |  | 10.1 to 20 | 0-20 | Type I-II3 | 0%
|  |  | 10.1 to 20 | 21-40 | Type V | 11%
|  |  | 10.1 to 20 | 21-40 | Type III-IV2 | 6%
|  |  | 10.1 to 20 | 21-40 | Type III-IV3 | 1%
|  |  | 10.1 to 20 | 21-40 | Type I-II2 | 4%
|  |  | 10.1 to 20 | 21-40 | Type I-II3 | 0%
|  |  | 10.1 to 20 | 41-60 | Type V | 12%
|  |  | 10.1 to 20 | 41-60 | Type III-IV2 | 7%
|  |  | 10.1 to 20 | 41-60 | Type III-IV3 | 2%
|  |  | 10.1 to 20 | 41-60 | Type I-II2 | 5%
|  |  | 10.1 to 20 | 41-60 | Type I-II3 | 0%
|  |  | 10.1 to 20 | 61-80 | Type V | 13%
|  |  | 10.1 to 20 | 61-80 | Type III-IV2 | 8%
|  |  | 10.1 to 20 | 61-80 | Type III-IV3 | 3%
|  |  | 10.1 to 20 | 61-80 | Type I-II2 | 6%
|  |  | 10.1 to 20 | 61-80 | Type I-II3 | 1%
|  |  | 10.1 to 20 | 81-100 | Type V | 14%
|  |  | 10.1 to 20 | 81-100 | Type III-IV2 | 9%
|  |  | 10.1 to 20 | 81-100 | Type III-IV3 | 4%
|  |  | 10.1 to 20 | 81-100 | Type I-II2 | 7%
|  |  | 10.1 to 20 | 81-100 | Type I-II3 | 2%
|  |  | 10.1 to 20 | Over 100 | Type V | 15%
|  |  | 10.1 to 20 | Over 100 | Type III-IV2 | 10%
|  |  | 10.1 to 20 | Over 100 | Type III-IV3 | 5%
|  |  | 10.1 to 20 | Over 100 | Type I-II2 | 8%
|  |  | 10.1 to 20 | Over 100 | Type I-II3 | 3%
|  |  | 20.1 to 30 | 0-20 | All Types | 0%
|  |  | 20.1 to 30 | 21-40 | Type V | 2%
|  |  | 20.1 to 30 | 21-40 | Type III-IV2 | 1%
|  |  | 20.1 to 30 | 21-40 | Type III-IV3 | 0%
|  |  | 20.1 to 30 | 21-40 | Type I-II2 | 0%
|  |  | 20.1 to 30 | 21-40 | Type I-II3 | 0%
|  |  | 20.1 to 30 | 41-60 | Type V | 4%
|  |  | 20.1 to 30 | 41-60 | Type III-IV2 | 2%
|  |  | 20.1 to 30 | 41-60 | Type III-IV3 | 0%
|  |  | 20.1 to 30 | 41-60 | Type I-II2 | 1%
|  |  | 20.1 to 30 | 41-60 | Type I-II3 | 0%
|  |  | 20.1 to 30 | 61-80 | Type V | 6%
|  |  | 20.1 to 30 | 61-80 | Type III-IV2 | 3%
|  |  | 20.1 to 30 | 61-80 | Type III-IV3 | 1%
|  |  | 20.1 to 30 | 61-80 | Type I-II2 | 2%
|  |  | 20.1 to 30 | 61-80 | Type I-II3 | 0%
|  |  | 20.1 to 30 | 81-100 | Type V | 8%
|  |  | 20.1 to 30 | 81-100 | Type III-IV2 | 4%
|  |  | 20.1 to 30 | 81-100 | Type III-IV3 | 2%
|  |  | 20.1 to 30 | 81-100 | Type I-II2 | 3%
|  |  | 20.1 to 30 | 81-100 | Type I-II3 | 0%
|  |  | 20.1 to 30 | Over 100 | Type V | 10%
|  |  | 20.1 to 30 | Over 100 | Type III-IV2 | 5%
|  |  | 20.1 to 30 | Over 100 | Type III-IV3 | 3%
|  |  | 20.1 to 30 | Over 100 | Type I-II2 | 4%
|  |  | 20.1 to 30 | Over 100 | Type I-II3 | 0%
|  |  | Over 30 m | All sizes | All Types (Over 30m) | 0%

## Read me
City of Barrie Fire Flow Calculator Per Fire Underwriters Survey (2020) (Important Notes)
Required user Input
Tabs marked with an asterisk (*) require user input. All required fields within these tabs must be completed to ensure accurate fire flow calculations. Users shall confirm that the information entered reflects the proposed building configuration and available design data.
Step B - Building Configuration Inputs
Users must enter the applicable building information under Step B, including: - Floors Above Grade - Total Floor Area (m²) - Percentage of Area Considered (%) These inputs shall be adjusted as necessary to accurately represent the configuration and distribution of the proposed building. Care should be taken to ensure that the total area and percentage allocations are consistent with submitted plans or design documents.
Step F – Exposure Adjustment (Table 5 vs. Table 6)
Where sufficient building information is available, the exposure adjustment shall be determined in accordance with FUS 2020 (Table 6). In cases where detailed building information is not available, users shall apply the exposure adjustment using FUS (Table 5) as a conservative or preliminary approach.
Optional Inputs and Dropdown Selections
For fields that include dropdown selections (e.g., Exposure Adjustment, Sprinkler Protection), users shall only select an option where applicable to the building under review. If a parameter does not apply, the field may be left blank or the default “Select Here” option may be retained. Users should avoid selecting values that do not accurately represent the building conditions, as this may impact the validity of the results.
Use and Limitations of the FUS Calculator
This FUS Calculator is intended as a supporting tool for preliminary assessment only. Results must be reviewed by a qualified professional and do not replace the requirements or alternative methods permitted under the Ontario Building Code (OBC).